## Rate Card
FIRE DOOR REMEDIAL WORKS — RATE CARD ¦ Jay Davis / WestPark Interiors
MOCK RATES — FOR DEVELOPMENT/TESTING ONLY. Alex to replace with actual rates. Yellow = input cells.
Updated 19 March 2026: B11 (lipping repair) and B12 (leaf void infill) added. Height band variants on A-series. These cover ART 01 and ART 02 in the EAS/FireDNA system.
CODE | DESCRIPTION | UNIT | MAT'S | LABOUR | T & J | HUMP | TOTAL RATE | NOTES
A — FULL DOOR REPLACEMENT (supply & fit certified fire door set including frame)
A01 | FD30 — Single Leaf, Paint Grade, Height up to 2040mm | no | 320 | 180 | 25 | 30 |  | Standard height — most common
A02 | FD30 — Single Leaf, Paint Grade, Height 2040–2400mm | no | 370 | 200 | 25 | 30 |  | Height uplift band
A03 | FD30 — Single Leaf, Paint Grade, Height 2400–2730mm | no | 420 | 220 | 25 | 35 |  | Tallest standard band
A04 | FD30 — Double Leaf, Paint Grade, Height up to 2040mm | no | 580 | 280 | 40 | 50 |  | Double leaf
A05 | FD30S — Single Leaf, Paint Grade + Smoke Seals, Height up to 2040mm | no | 380 | 190 | 25 | 30 |  | FD30S = FD30 + seals
A06 | FD30S — Single Leaf, Paint Grade + Smoke Seals, Height 2040–2400mm | no | 430 | 210 | 25 | 30 |  | Height uplift
A07 | FD30S — Single Leaf, Paint Grade + Smoke Seals, Height 2400–2730mm | no | 480 | 230 | 25 | 35 |  | Tallest band
A08 | FD30S — Double Leaf, Paint Grade + Smoke Seals, Height up to 2040mm | no | 650 | 300 | 40 | 50 |  | Double leaf FD30S
A09 | FD60S — Single Leaf, Paint Grade + Smoke Seals, Height up to 2040mm | no | 480 | 220 | 30 | 35 |  | 60-min — required by fire strategy
A10 | FD60S — Single Leaf, Paint Grade + Smoke Seals, Height 2040–2400mm | no | 540 | 240 | 30 | 35 |  | Height uplift
A11 | FD60S — Double Leaf, Paint Grade + Smoke Seals, Height up to 2040mm | no | 780 | 340 | 45 | 55 |  | Double leaf FD60S
A12 | E/O Hardwood Veneer Finish — any size (uplift per door) | no | 120 | 0 | 0 | 0 |  | On top of base rate
A13 | E/O External Grade Specification — weathered locations | no | 90 | 0 | 0 | 0 |  | On top of base rate
A14 | E/O Fire-Rated Vision Panel up to 300 x 600mm | no | 85 | 40 | 5 | 5 |  | Supply & fit fire-rated glazing
A15 | E/O Fire-Rated Vision Panel over 300 x 600mm | no | 130 | 55 | 5 | 5 |  | Larger vision panel
B — REMEDIAL WORKS (no door replacement — note: does NOT produce a certified fire door set)
B01 | Supply & fit intumescent + smoke seals — head, jambs, meeting edges | no | 45 | 65 | 5 | 5 |  | Most common remedial action
B02 | Supply & fit intumescent seals only — no smoke seal | no | 30 | 50 | 5 | 5 |  | Lower spec
B03 | Replace overhead door closer — supply & fit, CE-marked BS EN 1154 | no | 85 | 70 | 5 | 10 |  | Standard closer replacement
B04 | Replace / fix hinge set — screws or full replacement, BS EN 1935 Grade 11 | no | 35 | 45 | 5 | 5 |  | Check whether screws or full hinge needed
B05 | Replace lever handles / latch set — supply & fit, CE-marked ironmongery | no | 40 | 45 | 5 | 5 |  | SSS finish unless specified
B06 | Fire-stop frame-to-wall gap — intumescent mastic / ablative batt | no | 25 | 55 | 5 | 5 |  | Per door
B07 | Add or replace fire door signage — correct type per door (Keep Shut / Keep Locked) | no | 12 | 25 | 3 | 0 |  | Per door — 2 signs per leaf
B08 | Supply & fit electromagnetic hold-open device — fire alarm linked | no | 180 | 120 | 10 | 15 |  | Requires electrical connection
B09 | Replace threshold / automatic drop seal | no | 55 | 60 | 5 | 5 |  | Per door
B10 | Adjust / re-hang door leaf — binding, distortion, incorrect gaps, snagging on floor | no | 0 | 75 | 5 | 5 |  | Labour only
B11 | Door lipping repair — damaged / missing lipping re-lipped with hardwood (min 640kg/m3) *** NEW *** | no | 40 | 85 | 5 | 10 |  | Covers ART 01 in EAS/FireDNA system. Common fault — appears on ~20% of doors surveyed.
B12 | Door leaf void infill — repair hole/void from removed hardware using hardwood timber insert *** NEW *** | no | 35 | 75 | 5 | 10 |  | Covers ART 02 in EAS/FireDNA system. Appears frequently on tenant doors. Per hole/void.
C — PRELIMINARIES & ANCILLARIES
C01 | Mobilisation / Site setup — fixed call-out per visit | visit | 0 | 120 | 20 | 30 |  | Travel, van, tools, PPE
C02 | Waste removal & disposal — per door (average) | no | 15 | 25 | 0 | 10 |  | Removed doors, packaging, debris
C03 | Certification & completion documentation — per door | no | 0 | 35 | 5 | 0 |  | Photo record, cert, handover pack
C04 | Out-of-hours uplift — per day if required | day | 0 | 200 | 0 | 0 |  | Evening / weekend premium
C05 | Scaffold / access equipment — PROVISIONAL | item | 0 | 0 | 0 | 0 |  | Where standard access not possible

## Door Schedule
FIRE DOOR REMEDIAL WORKS — DOOR SCHEDULE ¦ AI-populated from survey PDF or Excel
Survey: AlphaSights Thames Court ¦ EAS Interiors Ltd ¦ BM TRADA 1470 ¦ 6 March 2026 ¦ 39 doors across Level 2 & Level 3
DOOR ID | LOCATION | DOOR TYPE | CURRENT RATING | LEAF CONFIG | LEAF SIZE | FINISH | SEALS | CLOSER | VISION PANEL | ACTION DESCRIPTION | SEVERITY | DUE DATE | OPT A REMEDIAL? | OPT B REPLACE? | OPT B BASE ITEM | QTY | E/O OVERSIZE? | E/O HARDWOOD? | E/O EXTERNAL? | E/O VISION? | NOTES / FLAGS
Floor 1-Floor 1-Door-2 | Floor 1 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Door gaps; Door, frame, and securing wall; Hinges, locks and other ironmongery; Door Glass where fitted; Strips and seals (if present*); Self-closer; Evidence of Doors wedged open; Comments | [5 empty] | B04 | B04, B03, B06 | NO | NO | NO | NO | ARTs: 01,02,04,19
Floor 1-Floor 1-Door-3 | Floor 1 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Hinges missing screws; Missing seal at top of door, where self-closer replaced; Comm's Room | [5 empty] | B04 | B04, B03 | NO | NO | NO | NO | ARTs: 02,05
Floor 1-Floor 1-Door-4 | Floor 1 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Requires adjustment to overcome latch.; Wedge noted - staff present stated only when room in use.; Cleaners cupboard | [5 empty] | B05 | B05 | NO | NO | NO | NO | ARTs: 04,11,16
Floor 1-Floor 1-Door-5 | Floor 1 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Requires adjustment to overcome latch.; Door is kept shut - small cupboard | [5 empty] | B05 | B05 | NO | NO | NO | NO | ARTs: 04,10,11,22
Floor 1-Floor 1-Door-6 | Floor 1 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Intumescent strip has been painted over; Not marked up as 'Fire Door'. - PDU Room | [5 empty] | B02 | B02 | NO | NO | NO | NO | ARTs: 04,10
Floor 1-Floor 1-Door-7 | Floor 1 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Coming away on the bottom edge; Perco double chains noted in use on door; Kitchen | [6 empty] | MANUAL REVIEW | NO | NO | NO | NO | ARTs: 04,13
Floor 1-Floor 1-Door-8 | Floor 1 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Not Fitted; None fitted.; Not Fitted; Kept locked shut. - Plant Room | [5 empty] | B05 | B05 | NO | NO | NO | NO | ARTs: 02,16,19
Floor 1-Floor 1-Door-9 | Floor 1 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Not Fitted; Intumescent only.; Not Fitted; Kept closed. | [5 empty] | B02 | B02 | NO | NO | NO | NO | ARTs: 02,04,16,19
Floor 1-Floor 1-Door-10 | Floor 1 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Unable to open door and check.; Not Fitted; Unable to open door and check.; Unable to open door and check.; Access hatch to service riser for maintenance only. | [6 empty] | MANUAL REVIEW | NO | NO | NO | NO | ARTs: 02,04,13
Floor 1-Floor 1-Door-11 | Floor 1 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Not Fitted; Damage to smoke seal; Kitchen holding area and kitchen staff changing areas | [6 empty] | MANUAL REVIEW | NO | NO | NO | NO | No actions required
Floor 2-Floor 2-Door-2 | Floor 2 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Door gaps; Door, frame, and securing wall; Hinges, locks and other ironmongery; Door Glass where fitted; Strips and seals (if present*); Self-closer; Evidence of Doors wedged open; Comments | [5 empty] | B04 | B04, B03, B06 | NO | NO | NO | YES | ARTs: 13,19,22
Floor 2-Floor 2-Door-3 | Floor 2 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Hinges missing screws; Not Fitted; Plant room kept locked shut. | [5 empty] | B05 | B05, B04 | NO | NO | NO | YES | ARTs: 02,10,19
Floor 2-Floor 2-Door-4 | Floor 2 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Unable to open door fully and check.; Unable to open fully door and check.; Unable to open fully door and check.; Unable to open door fully. Marked as store. | [6 empty] | MANUAL REVIEW | NO | NO | NO | NO | ARTs: 04,13,19
Floor 3-Floor 3-Door-2 | Floor 3 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Door gaps; Door, frame, and securing wall; Hinges, locks and other ironmongery; Door Glass where fitted; Strips and seals (if present*); Self-closer; Evidence of Doors wedged open; Comments | [5 empty] | B04 | B04, B03, B06 | NO | NO | NO | YES | ARTs: 02
Floor 3-Floor 3-Door-3 | Floor 3 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Not Fitted; Intumescent only.; Unable to open door to check; Electrical cupboard. Could only open right hand door due to location of drinks cabinet. | [5 empty] | B02 | B02 | NO | NO | NO | NO | ARTs: 04,10
Floor 3-Floor 3-Door-4 | Floor 3 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Not Fitted; Smoke seal worn on top edge; Wedge noted; Level 3 plant room | [6 empty] | MANUAL REVIEW | NO | NO | NO | YES | ARTs: 02,10
Floor 3-Floor 3-Door-5 | Floor 3 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Not closing as catching on floor.; Fire door exit from office into corridor | [6 empty] | MANUAL REVIEW | NO | NO | NO | NO | ARTs: 10
Floor 3-Floor 3-Door-6 | Floor 3 | From Survey | Unknown | Single Leaf | Unknown | Paint | To Check | To Check | Unable to open door to check.; Not Fitted; Unable to open door to check.; Unable to open door to check; Service access hatch door - no markings/labels. | [5 empty] | B07 | B07 | NO | NO | NO | NO | ARTs: 04,16,21,22
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 11,13
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 04,16,21
[16 empty] | 1 | NO | NO | NO | YES | No actions required
[16 empty] | 1 | NO | NO | NO | YES | ARTs: 02,04,08,19,21
[16 empty] | 1 | NO | NO | NO | YES | ARTs: 01,04,19,21
[16 empty] | 1 | NO | NO | NO | NO | No actions required
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 13
[16 empty] | 1 | NO | NO | NO | NO | No actions required
[16 empty] | 1 | NO | NO | NO | YES | No actions required
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 04,16,19,21
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 18 ¦ REPLACE — dims: 2650x950x70mm
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 10
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 18 ¦ REPLACE — dims: 2650x1810x135mm
[16 empty] | 1 | NO | NO | NO | YES | ARTs: 04
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 04
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 02,04,16
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 13
[16 empty] | 1 | NO | NO | NO | YES | No actions required
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 01,04,13,21
[16 empty] | 1 | NO | NO | NO | NO | ARTs: 05,11,19
[16 empty] | 1 | NO | NO | NO | YES | ARTs: 08,11,19
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=Missing seal at top of door, where self-, closer=OK
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=OK, closer=Requires adjustment to overcome latch. ¦ WEDGED: Wedge noted - staff present stated only when room in use.
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=OK, closer=Requires adjustment to overcome latch.
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=Intumescent strip has been painted over, closer=OK
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=Coming away on the bottom edge, closer=Perco double chains noted in use on door ¦ FLAG: Hold-open device in use — B08 may be needed
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=None fitted., closer=Not Fitted
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=Intumescent only., closer=Not Fitted
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=Unable to open door and check., closer=Unable to open door and check. ¦ FLAG: Unable to inspect hinges/ironmongery ¦ FLAG: Unable to inspect seals ¦ FLAG: Unable to inspect closer
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=Damage to smoke seal , closer=OK
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=OK, closer=OK
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=Unable to open fully door and check., closer=Unable to open fully door and check. ¦ FLAG: Unable to inspect hinges/ironmongery ¦ FLAG: Unable to inspect seals ¦ FLAG: Unable to inspect closer
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=Intumescent only., closer=Unable to open door to check ¦ FLAG: Unable to inspect closer
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=Smoke seal worn on top edge, closer=OK ¦ WEDGED: Wedge noted
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=OK, closer=Not closing as catching on floor.
[16 empty] | 1 | NO | NO | NO | NO | Type 2 survey. Faults: seals=Unable to open door to check., closer=Unable to open door to check ¦ FLAG: Unable to inspect hinges/ironmongery ¦ FLAG: Unable to inspect seals ¦ FLAG: Unable to inspect closer

## Quote Sheet
FIRE DOOR REMEDIAL WORKS — QUOTE SHEET
Quote Ref: | WP-2026-001 | [14 empty] | TARGET MARGIN: | 35%
Date: | 06/03/2026
Client: | Natixis CITYSPACE
Site: | Thames Court
Building: | 1 Queenhithe, London EC4V 3DX
ITEM | DESCRIPTION | QTY | UNIT | RATE | TOTAL | MAT'S | MAT'S TOTAL | LAB | LAB TOTAL | T & J | T & J TOTAL | HUMP | HUMP TOTAL | TOTAL COST | PROFIT | % MARGIN | % PROFIT
OPT A | OPTION A — Remedial Works Only ¦ Does NOT produce a certified fire door set
Quantities = doors marked YES in Door Schedule Option A column. Type 2 (Excel) surveys populate this section.
A.01 | Supply & fit intumescent + smoke seals |  | no
A.02 | Supply & fit intumescent seals only |  | no
A.03 | Replace overhead door closer — supply & fit |  | no
A.04 | Replace / fix hinge set |  | no
A.05 | Replace lever handles / latch set |  | no
A.06 | Fire-stop frame-to-wall gap |  | no
A.07 | Add / replace fire door signage |  | no
A.08 | Supply & fit electromagnetic hold-open device |  | no
A.09 | Replace threshold / drop seal |  | no
A.10 | Adjust / re-hang door leaf |  | no
A.11 | Door lipping repair (hardwood re-lip) *** B11 |  | no
A.12 | Door leaf void infill (hardwood timber insert) *** B12 |  | no
OPT B | OPTION B — Full Door Replacement ¦ Certified fire door sets — RECOMMENDED
Quantities = doors marked YES in Door Schedule Option B column, by BASE ITEM code. Type 2 surveys show PENDING — fire strategy required.
B.01 | FD30 — Single Leaf, Paint Grade, Height up to 2040mm |  | no
B.02 | FD30 — Single Leaf, Paint Grade, Height 2040–2400mm |  | no
B.03 | FD30 — Single Leaf, Paint Grade, Height 2400–2730mm |  | no
B.04 | FD30 — Double Leaf, Paint Grade, Height up to 2040mm |  | no
B.05 | FD30S — Single Leaf, Paint Grade + Smoke Seals, Height up to 2040mm |  | no
B.06 | FD30S — Single Leaf, Paint Grade + Smoke Seals, Height 2040–2400mm |  | no
B.07 | FD30S — Single Leaf, Paint Grade + Smoke Seals, Height 2400–2730mm |  | no
B.08 | FD30S — Double Leaf, Paint Grade + Smoke Seals, Height up to 2040mm |  | no
B.09 | FD60S — Single Leaf, Paint Grade + Smoke Seals, Height up to 2040mm |  | no
B.10 | FD60S — Single Leaf, Paint Grade + Smoke Seals, Height 2040–2400mm |  | no
B.11 | FD60S — Double Leaf, Paint Grade + Smoke Seals, Height up to 2040mm |  | no
B.12 | E/O Hardwood Veneer Finish (per door) |  | no
B.13 | E/O External Grade Specification (per door) |  | no
B.14 | E/O Fire-Rated Vision Panel up to 300 x 600mm |  | no
B.15 | E/O Fire-Rated Vision Panel over 300 x 600mm |  | no
PRE | PRELIMINARIES & ANCILLARIES ¦ Applied to whichever option is chosen
P.01 | Mobilisation / Site setup (per visit) | 1 | visit
P.02 | Waste removal & disposal | 1 | no
P.03 | Certification & completion documentation | 1 | no
P.04 | Out-of-hours uplift (if required) | 1 | day
P.05 | Scaffold / access equipment — PROVISIONAL | 1 | item
OPTION A TOTAL
OPTION B TOTAL (RECOMMENDED)

## Material Call-Off
FIRE DOOR REMEDIAL WORKS — MATERIAL CALL-OFF ¦ Auto-generated on job win
IMPORTANT: Door sizes (leaf width and height) must be physically measured on site before ordering. All other components can be ordered from this list immediately.
B11 (lipping) and B12 (void infill) added to components list. Quantities for these are counted from Door Schedule — typical rate approx 20% of surveyed doors.
DOOR ID | LOCATION | COMPONENT | QTY | UNIT | ORDER STATUS | SUPPLIER | COST EX VAT | NOTES / FLAGS
FIRE DOORS — SIZES MUST BE MEASURED ON SITE BEFORE ORDERING (Option B only)
A12-L3 | Core 5 tenant door to WCs | FD60S Single Leaf — MEASURE BEFORE ORDER | 1 | no | Pending |  |  | Survey dims: 2650x950x70mm — VERIFY ON SITE
A14-L3 | Core 4 tenant DB riser | FD30 Double Leaf — MEASURE BEFORE ORDER | 1 | no | Pending |  |  | Survey dims: 2650x1810x135mm — VERIFY ON SITE
COMPONENTS — READY TO ORDER (quantities aggregated across all doors)
ALL | All doors | Overhead door closer — CE-marked, BS EN 1154 |  | no | Ready to order |  |  | Count from Door Schedule col I
ALL | All doors | Hinge set (3 hinges) — BS EN 1935 Grade 11 |  | sets | Ready to order |  |  | One set per door requiring hinge work
ALL | All doors | Intumescent + smoke seals — 10mm x 4mm double fin white |  | doors | Ready to order |  |  | One linear kit per door
ALL | All doors | Intumescent seals only (no smoke seal) |  | doors | Ready to order |  |  | Doors with seals action but no smoke seal
ALL | All doors | Fire door signage — 'Keep Shut' / 'Keep Locked' |  | no | Ready to order |  |  | 2 signs per door (both sides)
ALL | All doors | Drop seal / automatic threshold seal | 0 | no | Check survey |  |  | Count from doors with B09 code
ALL | All doors | Lever handle / latch set — CE-marked, SSS finish | 0 | no | Check survey |  |  | Count from doors with B05 code
ALL | All doors | Intumescent mastic — fire-stopping frame gaps | 0 | items | Check survey |  |  | Count from doors with B06 code
ALL | All doors | Hardwood lipping material (B11) — min density 640kg/m3 |  | doors | Ready to order |  |  | NEW: count from B11-coded doors
ALL | All doors | Hardwood timber inserts for void infill (B12) |  | doors | Ready to order |  |  | NEW: count from B12-coded doors. Per void/hole.

## Client Summary
FIRE DOOR REMEDIAL WORKS — CLIENT PROPOSAL SUMMARY
Client:
Site:
Building:
Date:
Quote Ref:
SECTION | DESCRIPTION | NET COST | OPTION A TOTAL | OPTION B TOTAL
A | Remedial Works (seals, closers, hinges, fire-stopping, signage, lipping, void infill) |  |  | N/A — Option B only
B | Full Door Replacements (certified fire door sets — RECOMMENDED) |  | N/A — Option A only
PRE | Preliminaries & Ancillaries
TOTAL INVESTMENT
COMPLIANCE NOTE Option A — Remedial Works Only: These works do not produce a certified fire door set. Fire resistance relies on landlord declaration only. Cheaper but limited assurance. Option B — Full Replacement (RECOMMENDED): Certified fire door sets installed per fire strategy. Full BS-certified compliance, demonstrable liability protection. This is what the assessor recommends. Note: Where input survey is Type 2 (Excel) format, Option B total may show 0 — fire strategy drawings are required to confirm the intended fire rating per door set before replacement can be priced.
Achieved Margins: